## Submissions
Submission Date | Name of Tester | Select Test Area | Select House Unit to Test | Select Annexe Unit to Test | Select Mews Unit to Test | Select Barn Unit to Test | Test Result | Report Fault | Details of Fault
2018-12-05 09:35 | Mario Fuchs | Barn |  |  |  | 205 : Kitchen | FAIL | Lamp blown
2018-12-05 09:34 | Mario Fuchs | Barn |  |  |  | 207 : Mezzanine | PASS
2018-12-05 09:34 | Mario Fuchs | Barn |  |  |  | 206 : Corridor O/S Toilets | PASS
2018-12-05 09:34 | Mario Fuchs | Barn |  |  |  | 204 : Board Room | PASS
2018-12-05 09:34 | Mario Fuchs | Barn |  |  |  | 203 : Main Lobby (O/S Kitchen) | PASS
2018-12-05 09:34 | Mario Fuchs | Barn |  |  |  | 202 : Main Lobby (O/S Board Room) | PASS
2018-12-05 09:33 | Mario Fuchs | Barn |  |  |  | 201 : Over Main Front Door | FAIL | Other known fault | Battery not working
2018-12-05 09:31 | Mario Fuchs | Mews |  |  | 61 : Mews 1st Floor Flat 8 outside walkway |  | PASS
2018-12-05 09:31 | Mario Fuchs | Mews |  |  | 60 : Mews 1st Floor Flat 8 inside on ceiling |  | PASS
2018-12-05 09:31 | Mario Fuchs | Mews |  |  | 59 : Mews 1st Floor Flat 7 outside walkway balcony |  | PASS
2018-12-05 09:31 | Mario Fuchs | Mews |  |  | 58 : Mews 1st Floor Flat 7 outside walkway |  | PASS
2018-12-05 09:31 | Mario Fuchs | Mews |  |  | 57 : Mews 1st Floor Flat 7 inside on ceiling |  | PASS
2018-12-05 09:30 | Mario Fuchs | Mews |  |  | 56 : Mews 1st Floor Flat 6 outside walkway balcony |  | PASS
2018-12-05 09:30 | Mario Fuchs | Mews |  |  | 55 : Mews 1st Floor Flat 6 outside walkway |  | PASS
2018-12-05 09:30 | Mario Fuchs | Mews |  |  | 54 : Mews 1st Floor Flat 6 inside on ceiling |  | PASS
2018-12-05 09:30 | Mario Fuchs | Mews |  |  | 53 : Mews 1st Floor Flat 5 outside walkway |  | PASS
2018-12-05 09:29 | Mario Fuchs | Mews |  |  | 52 : Mews 1st Floor Flat 5 inside on ceiling |  | FAIL | Other known fault | Battery end of life no light when testing
2018-12-05 09:27 | Mario Fuchs | Mews |  |  | 51 : Mews Stairwell 1st Floor |  | PASS
2018-12-05 09:27 | Mario Fuchs | Mews |  |  | 50 : Mews Stairwell Middle |  | PASS
2018-12-05 09:27 | Mario Fuchs | Mews |  |  | 49 : Mews Stairwell Ground |  | PASS
2018-12-05 09:27 | Mario Fuchs | Mews |  |  | 48 : Mews Ground Floor Flat 4 outside walkway |  | PASS
2018-12-05 09:27 | Mario Fuchs | Mews |  |  | 48 : Mews Ground Floor Flat 4 outside walkway |  | PASS
2018-12-05 09:27 | Mario Fuchs | Mews |  |  | 47 : Mews Ground Floor Flat 4 inside ceiling |  | PASS
2018-12-05 09:26 | Mario Fuchs | Mews |  |  | 46 : Mews Ground Floor Flat 3 outside walkway |  | PASS
2018-12-05 09:26 | Mario Fuchs | Mews |  |  | 45 : Mews Ground Floor Flat 3 inside on ceiling |  | PASS
2018-12-05 09:26 | Mario Fuchs | Mews |  |  | 44 : Mews Ground Floor Stairwell Exit |  | PASS
2018-12-05 09:26 | Mario Fuchs | Mews |  |  | 43 : Mews Ground Floor Flat 2 outside walkway |  | PASS
2018-12-05 09:26 | Mario Fuchs | Mews |  |  | 42 : Mews Ground Floor Flat 2 inside on ceiling |  | PASS
2018-12-05 09:25 | Mario Fuchs | Mews |  |  | 41 : Mews Ground Floor Flat 1 outside walkway |  | PASS
2018-12-05 09:25 | Mario Fuchs | Mews |  |  | 40 : Mews Ground Floor Flat 1 inside on ceiling |  | PASS
2018-12-05 09:25 | Mario Fuchs | Mews |  |  | 39 : Mews Dining Room Exit outside double doors |  | PASS
2018-12-05 09:25 | Mario Fuchs | Mews |  |  | 38 : Mews Dining Room Front |  | PASS
2018-12-05 09:24 | Mario Fuchs | Mews |  |  | 37 : Mews Dining Room Middle |  | PASS
2018-12-05 09:24 | Mario Fuchs | Mews |  |  | 36 : Mews Dining Room Rear |  | PASS
2018-12-05 09:23 | Mario Fuchs | Annexe |  | 83A Annex 1st Floor End Stair Case above door |  |  | PASS
2018-12-05 09:23 | Mario Fuchs | Annexe |  | 83 Annex 1st Floor End Stair Case above door |  |  | PASS
2018-12-05 09:23 | Mario Fuchs | Annexe |  | 83 Annex 1st Floor End Stair Case above door |  |  | PASS
2018-12-05 09:23 | Mario Fuchs | Annexe |  | 82 Annex 1st Floor Corridor above door outside room 27 |  |  | PASS
2018-12-05 09:23 | Mario Fuchs | Annexe |  | 81 Annex 1st Floor Corridor opposite clinical room above door |  |  | PASS
2018-12-05 09:22 | Mario Fuchs | Annexe |  | 80 Annex 1st Floor Corridor ceiling outside room 26 |  |  | PASS
2018-12-05 09:22 | Mario Fuchs | Annexe |  | 79 Annex 1st Floor Corridor ceiling outside room 23 |  |  | PASS
2018-12-05 09:22 | Mario Fuchs | Annexe |  | 78 : Annex 1st Floor Corridor Stairwell above door opposite room 22 other side |  |  | PASS
2018-12-05 09:22 | Mario Fuchs | Annexe |  | 77 : Annex 1st Floor Corridor Stairwell above door opposite room 22 |  |  | PASS
2018-12-05 09:22 | Mario Fuchs | Annexe |  | 76 : Annex 1st Floor Corridor Nurse Office above door other side |  |  | PASS
2018-12-05 09:21 | Mario Fuchs | Annexe |  | 75 : Annex 1st Floor Corridor Nurse Office above door |  |  | PASS
2018-12-05 09:21 | Mario Fuchs | Annexe |  | 74 : Annex 1st Floor Corridor outside bed pan wash room |  |  | PASS
2018-12-05 09:21 | Mario Fuchs | Annexe |  | 73 : Annex 1st Floor Dormant next to door |  |  | PASS
2018-12-05 09:21 | Mario Fuchs | Annexe |  | 72 : Annex 1st Floor Contestant outside above door |  |  | PASS
2018-12-05 09:21 | Mario Fuchs | Annexe |  | 35B : Annex Ground Floor End Corridor Stairwell below fuse board |  |  | PASS
2018-12-05 09:20 | Mario Fuchs | Annexe |  | 35A : Annex Ground Floor End Corridor Stairwell above door |  |  | PASS
2018-12-05 09:20 | Mario Fuchs | Annexe |  | 34 : Annex Ground Floor End Corridor Fire Exit above door |  |  | PASS
2018-12-05 09:20 | Mario Fuchs | Annexe |  | 33 : Annex Ground Floor End Corridor Room 38 outside above door |  |  | PASS
2018-12-05 09:20 | Mario Fuchs | Annexe |  | 32 : Annex Sun Lounge above double doors |  |  | PASS
2018-12-05 09:20 | Mario Fuchs | Annexe |  | 31 : Annex Sun Lounge above door |  |  | PASS
2018-12-05 09:20 | Mario Fuchs | Annexe |  | 30 : Annex Ground Floor Corridor Stairwell above door outside |  |  | PASS
2018-12-05 09:19 | Mario Fuchs | Annexe |  | 29 : Annex Ground Floor Sitting Room outside above door |  |  | PASS
2018-12-05 09:19 | Mario Fuchs | Annexe |  | 28 : Annex Ground Floor Corridor Physio Room outside above door |  |  | PASS
2018-12-05 09:19 | Mario Fuchs | Annexe |  | 27 : Annex Ground Floor Corridor Room 43 outside above door |  |  | PASS
2018-12-05 09:19 | Mario Fuchs | Annexe |  | 26 : Annex Ground Floor Corridor above lift motor room door |  |  | PASS
2018-12-05 09:19 | Mario Fuchs | Annexe |  | 25 : Annex Ground Floor Entrance above door |  |  | PASS
2018-12-05 09:18 | Mario Fuchs | Annexe |  | 24 : Annex Ground Floor Lift Motor Room inside |  |  | PASS
2018-12-05 09:18 | Mario Fuchs | House | 95 House 2nd Floor Lakeview Corridor Stairwell ceiling |  |  |  | PASS
2018-12-05 09:17 | Mario Fuchs | House | 94 House 2nd Floor Lakeview Corridor Fire Exit above door |  |  |  | PASS
2018-12-05 09:17 | Mario Fuchs | House | 93 House 2nd Floor Lakeview Corridor end on the wall |  |  |  | PASS
2018-12-05 09:17 | Mario Fuchs | House | 92 House 2nd Floor Lakeview Corridor opposite window |  |  |  | PASS
2018-12-05 09:17 | Mario Fuchs | House | 91 House 2nd Floor Corridor Lakeview Apartment above fire door |  |  |  | PASS
2018-12-05 09:17 | Mario Fuchs | House | 90 House 2nd Floor Hawthorn Corridor Fire Exit above door |  |  |  | PASS
2018-12-05 09:16 | Mario Fuchs | House | 89 House 2nd Floor Oakview Corridor Lift |  |  |  | PASS
2018-12-05 09:16 | Mario Fuchs | House | 88 House 2nd Floor Corridor Oakview Apartment above door |  |  |  | PASS
2018-12-05 09:16 | Mario Fuchs | House | 87 House 2nd Floor Hawthorn Corridor |  |  |  | PASS
2018-12-05 09:16 | Mario Fuchs | House | 86 House 2nd Floor Hawthorn Corridor |  |  |  | PASS
2018-12-05 09:15 | Mario Fuchs | House | 85 House 2nd Floor Hawthorn Apartment above door |  |  |  | PASS
2018-12-05 09:15 | Mario Fuchs | House | 84 House 2nd Floor Stairs top of staircase |  |  |  | PASS
2018-12-05 09:15 | Mario Fuchs | House | 71 House 1st Floor Pad Store outside above door |  |  |  | PASS
2018-12-05 09:15 | Mario Fuchs | House | 70 House 1st Floor Fire Exit Ramp above fire door |  |  |  | PASS
2018-12-05 09:14 | Mario Fuchs | House | 69 House 1st Floor Magnolia outside on ceiling |  |  |  | PASS
2018-12-05 09:14 | Mario Fuchs | House | 68 House 1st Floor Fire Alarm Panel stair case |  |  |  | PASS
2018-12-05 09:14 | Mario Fuchs | House | 67 House 1st Floor Matron's Office outside ceiling |  |  |  | PASS
2018-12-05 09:14 | Mario Fuchs | House | 66 House 1st Floor Top Stairs main hall |  |  |  | PASS
2018-12-05 09:14 | Mario Fuchs | House | 65 House 1st Floor Lift above door |  |  |  | PASS
2018-12-05 09:13 | Mario Fuchs | House | 64 House 1st Floor Wisteria Apartment outside above door |  |  |  | PASS
2018-12-05 09:13 | Mario Fuchs | House | 63 House 1st Floor Room 8 outside ceiling |  |  |  | PASS
2018-12-05 09:13 | Mario Fuchs | House | 62 House 1st Floor Winterfold Apartment ceiling bottom of stairs |  |  |  | PASS
2018-12-05 09:12 | Mario Fuchs | House | 23 Activities Corridor opposite single door |  |  |  | PASS
2018-12-05 09:12 | Mario Fuchs | House | 22 Activities Corridor Toilet middle of ceiling |  |  |  | PASS
2018-12-05 09:12 | Mario Fuchs | House | 21 Activities Room above single door |  |  |  | PASS
2018-12-05 09:12 | Mario Fuchs | House | 20 Activities Corridor Exit above first fire exit door |  |  |  | PASS
2018-12-05 05:02 | Mario Fuchs | House | 22 Activities Corridor Toilet middle of ceiling |  |  |  | PASS
2018-12-05 05:02 | Mario Fuchs | House | 22 Activities Corridor Toilet middle of ceiling |  |  |  | PASS
2018-12-05 05:01 | Mario Fuchs | House | 21 Activities Room above single door |  |  |  | PASS
2018-12-05 05:00 | Mario Fuchs | House | 20 Activities Corridor Exit above first fire exit door |  |  |  | PASS
2018-12-05 04:56 | Mario Fuchs | House | 19 Activities Corridor opposite kitchen |  |  |  | PASS
2018-12-05 04:55 | Mario Fuchs | House | 18 House Ground Floor Back Door above door |  |  |  | PASS
2018-12-05 04:55 | Mario Fuchs | House | 17 Activities Corridor Laundry ceiling above door |  |  |  | PASS
2018-12-05 04:49 | Mario Fuchs | House | 16 House Ground Floor Staff Room bottom of stair well |  |  |  | PASS
2018-12-05 04:48 | Mario Fuchs | House | 15 House Ground Floor Kitchen Corridor above door opposite staff toilet |  |  |  | PASS
2018-12-05 04:48 | Mario Fuchs | House | 14 : House Ground Floor Kitchen Corridor above door next to visitors toilet |  |  |  | PASS
2018-12-05 04:46 | Mario Fuchs | House | 13 : House Ground Floor Basement above door opposite side |  |  |  | PASS
2018-12-05 04:46 | Mario Fuchs | House | 12 : House Ground Floor Orangery above fire exit door |  |  |  | PASS
2018-12-05 04:08 | Mario Fuchs | House | 12 : House Ground Floor Orangery above fire exit door |  |  |  | PASS
2018-12-05 04:07 | Mario Fuchs | House | 11 : House Ground Floor Orangery Lift above door |  |  |  | PASS
2018-12-05 04:07 | Mario Fuchs | House | 10 : House Basement Training Room outside door |  |  |  | PASS
2018-12-05 04:07 | Mario Fuchs | House | 09 : House Basement Training Room Stair straight ahead |  |  |  | PASS
2018-12-05 04:06 | Mario Fuchs | House | 08 : House Ground Floor Willow Tree Apartment stair case below fuse board |  |  |  | PASS
2018-12-05 04:06 | Mario Fuchs | House | 07 : House Ground Floor Orangery Above Control Box |  |  |  | PASS
2018-12-05 04:03 | Mario Fuchs | House | 06 : House Ground Floor Terrace Apartment |  |  |  | PASS
2018-12-05 04:01 | Mario Fuchs | House | 05 : House Ground Floor Drawing Room above door main hall |  |  |  | PASS
2018-12-05 03:51 | Mario Fuchs | House | 04 : House Ground Floor Main Hall Balcony bottom stair look up |  |  |  | PASS
2018-12-05 03:41 | Mario Fuchs | House | 03 : House Ground Floor Old Front Door inside above door |  |  |  | FAIL | Other known fault | Battery doesn't keep charge light is on all time
2018-12-05 03:40 | Mario Fuchs | House | 02 : House Ground Floor Annex link corridor above exit sign |  |  |  | PASS
2018-12-05 03:39 | Mario Fuchs | House | 01 : House Ground Floor Front Door above front door |  |  |  | PASS